| LISTADO DE PRUEBAS |  |  |
| --- | --- | --- |
| 1. INSPECCION VISUAL | APLICA | NO APLICA |
| 2. TIEMPOS DE OPERACIÓN Y DISCORDANCIA DE FASES | APLICA | NO APLICA |

| # DATOS GENERALES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| CLIENTE: ANDE |  |  |  |  |  |
| OBRA/LUGAR: SUBESTACION CAPIATA |  |  |  |  |  |
| DESCRIPCION GENERAL |  |  |  |  |  |
| FABRICANTE: SIEMENS |  | TENSION ASIGNADA NORMAL: 24kV (VARIABLE) |  |  |  |
| TIPO: 8DA10 (VARIABLE) |  | CORRIENTE ASIGNADA NORMAL: 4000A (VARIABLE) |  |  |  |
| AÑO FABRICACION: 2023 (VARIABLE) |  | CORRIENTE DE CORTOCIRCUITO: 40kA (VARIABLE) |  |  |  |
| NUMERO DE SERIE: CV 563100 – 000020/001 (VARIABLE) |  | FRECUENCIA NOMINAL: 50Hz |  |  |  |
| 1. VERIFICACIÓN VISUAL |  |  |  |  |  |
| Elemento |  | Fase A |  | Fase B | Fase C |
| Estado de la base portante |  | Buen estado Mal estado |  | Buen estado Mal estado | Buen estado Mal estado |
| Estado de la unidad del mecanismo de accionamiento |  | Buen estado Mal estado |  | Buen estado Mal estado | Buen estado Mal estado |
| Estado de la unidad de mando |  | Buen estado Mal estado |  | Buen estado Mal estado | Buen estado Mal estado |
| Estado indicador de presión |  | Buen estado Mal estado |  | Buen estado Mal estado | Buen estado Mal estado |
| Comprobar la hermeticidad de los polos |  | Buen estado Mal estado |  | Buen estado Mal estado | Buen estado Mal estado |

| 2. TIEMPOS DE OPERACIÓN DE LOS CONTACTOS PRINCIPALES DEL INTERRUPTOR |  |  |  |
| --- | --- | --- | --- |
| Equipo Utilizado para la prueba (VARIABLE, PERO DEJAR COMO DEFAULT) |  |  |  |
| Descripción | Fabricante | Modelo – Serie No. | Fecha de la última calibración |
| Oscilógrafo | DV Power | CAT124A – 22U939 | 10-0CT-2025 (VARIABLE) |
| Ver reporte de pruebas del equipo, en anexo. |  |  |  |

OBSERVACIONES

Ninguna.

---------------------------------------------------------------ANEXO---------------------------------------------------------------------

| Timing test |  | O1 (Open test) |  |  |  |
| --- | --- | --- | --- | --- | --- |
| General parameters |  |  |  | Testing device settings |  |
| Execution date/Time |  |  | 2/17/2026 / 10:47 AM | Device model / Serial-no | CAT124A / - |
| Coil supply voltage |  |  |  | Transducer type | Digital transducer |
| Measuring time |  |  | 700 ms | Transducer on CBs phase-s | All three |
| Command pulse |  |  | 80 | Transducer transfer functions | 0mm:0deg |
| Resolution |  |  | 0.025 ms | Trigger source |  |
| Frequency |  |  | 50 Hz | BSG mode |  |

| Main contacts timing |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Open time(to) | 0 | 0 | 49.95 | ms | Correcto |
| Open time sync(dto) | 0 | 0 | 0.375 | ms | Correcto |
| Opening time |  |  |  |  |  |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Opening time - A | 0 | 0 | 49.95 | ms | Correcto |
| Opening time - B | 0 | 0 | 49.575 | ms | Correcto |
| Opening time - C | 0 | 0 | 49.7 | ms | Correcto |
| Opening coil result 1 |  |  |  |  |  |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Pick-up time | 0 | 0 | 34 | ms | Correcto |
| Ipmax | 0 | 0 | 1.24 | A | Correcto |

| Opening coil result 1 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Aux | 0 | 0 | 47.53 | ms | Correcto |
| De-energized coil | 0 | 0 | 48.75 | ms | Correcto |
| Imax | 0 | 0 | 1.73 | A | Correcto |

| Timing test | C1 (Close test) |  |  |  |
| --- | --- | --- | --- | --- |
| General parameters |  |  | Testing device settings |  |
| Execution date/Time |  | 2/17/2026 / 10:50 AM | Device model / Serial-no | CAT124A / - |
| Coil supply voltage |  |  | Transducer type | Digital transducer |
| Measuring time |  | 700 ms | Transducer on CBs phase-s | All three |
| Command pulse |  | 160 | Transducer transfer functions | 0mm:0deg |
| Resolution |  | 0.025 ms | Trigger source |  |
| Frequency |  | 50 Hz | BSG mode |  |

| Bounce time |  |  |
| --- | --- | --- |
| Designation | C1 | Unit |
| Bounce time-A | 1.925 | ms |
| Bounce time-B | 1.875 | ms |
| Bounce time-C | 1.925 | ms |

| Main contacts timing |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Close time(tc) | 0 | 0 | 62.925 | ms | Correcto |
| Close time sync(dtc) | 0 | 0 | 0.625 | ms | Correcto |
| Closing time |  |  |  |  |  |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Close time - A | 0 | 0 | 62.3 | ms | Correcto |
| Close time - B | 0 | 0 | 62.925 | ms | Correcto |
| Close time - C | 0 | 0 | 62.85 | ms | Correcto |

| Timing test | OCO1 (Open-Close-Open test) |  |  |  |
| --- | --- | --- | --- | --- |
| General parameters |  |  | Testing device settings |  |
| Execution date/Time |  | 2/17/2026 / 10:56 AM | Device model / Serial-no | CAT124A / - |
| Coil supply voltage |  |  | Transducer type | Digital transducer |
| Measuring time |  | 700 ms | Transducer on CBs phase-s | All three |
| Command pulse |  |  | Transducer transfer functions | 0mm:0deg |
| Resolution |  | 0.025 ms | Trigger source |  |
| Frequency |  | 50 Hz | BSG mode |  |

| Main contacts timing |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Open time(to) | 0 | 0 | 50.525 | ms | Correcto |
| Reclosing time | 0 | 0 | 362.75 | ms | Correcto |
| Reclosing time sync | 0 | 0 | 0.625 | ms | Correcto |
| O1 sync time | 0 | 0 | 0.325 | ms | Correcto |
| O2 sync time | 0 | 0 | 0.4 | ms | Correcto |
| Open-Close time(toc) | 0 | 0 | 311.6 | ms | Correcto |
| Close-Open time(tco) | 0 | 0 | 66.225 | ms | Correcto |
| Opening time |  |  |  |  |  |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Opening time - A | 0 | 0 | 50.525 | ms | Correcto |
| Opening time - B | 0 | 0 | 50.2 | ms | Correcto |
| Opening time - C | 0 | 0 | 50.275 | ms | Correcto |

| Timing test | CO1 (Close-Open test) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| General parameters |  |  | Testing device settings |  |  |
| Execution date/Time |  | 2/17/2026 / 10:58 AM | Device model / Serial-no | CAT124A / - |  |
| Coil supply voltage |  |  | Transducer type | Digital transducer |  |
| Measuring time |  | 700 ms | Transducer on CBs phase-s | All three |  |
| Command pulse |  |  | Transducer transfer functions | 0mm:0deg |  |
| Resolution |  | 0.025 ms | Trigger source |  |  |
| Frequency |  | 50 Hz | BSG mode |  |  |

| Main contacts timing |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Close time(tc) | 0 | 0 | 63.025 | ms | Correcto |
| Close time sync(dtc) | 0 | 0 | 0.65 | ms | Correcto |
| Close-Open time(tco) | 0 | 0 | 65.175 | ms | Correcto |
| Breaker O sync | 0 | 0 | 0.4 | ms | Correcto |
| Closing time |  |  |  |  |  |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Close time - A | 0 | 0 | 62.375 | ms | Correcto |
| Close time - B | 0 | 0 | 63.025 | ms | Correcto |
| Close time - C | 0 | 0 | 62.925 | ms | Correcto |

| Coil currents |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Coil | Min | Max | Closing coil1 | Closing coil2 | Closing coil3 | Unit | Pass/Check |
| Max current value | 0 | 0 | 1.601 | 0 | 0 | A | Correcto |
| Max current time | 0 | 0 | 44.625 | 0 | 0 | ms | Correcto |
| Coil currents |  |  |  |  |  |  |  |
| Coil | Min | Max | Opening coil1 | Opening coil2 | Opening coil3 | Unit | Pass/Check |
| Max current value | 0 | 0 | 1.739 | 0 | 0 | A | Correcto |
| Max current time | 0 | 0 | 120.275 | 0 | 0 | ms | Correcto |

| Timing test | O2 (Open test) |  |  |  |
| --- | --- | --- | --- | --- |
| General parameters |  |  | Testing device settings |  |
| Execution date/Time |  | 2/17/2026 / 11:04 AM | Device model / Serial-no | CAT124A / - |
| Coil supply voltage |  |  | Transducer type | Digital transducer |
| Measuring time |  | 700 ms | Transducer on CBs phase-s | All three |
| Command pulse |  | 80 | Transducer transfer functions | 0mm:0deg |
| Resolution |  | 0.025 ms | Trigger source |  |
| Frequency |  | 50 Hz | BSG mode |  |

| Main contacts timing |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Open time(to) | 0 | 0 | 51.175 | ms | Correcto |
| Open time sync(dto) | 0 | 0 | 0.425 | ms | - |
| Opening time |  |  |  |  |  |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Opening time - A | 0 | 0 | 51.175 | ms | - |
| Opening time - B | 0 | 0 | 50.75 | ms | - |
| Opening time - C | 0 | 0 | 50.9 | ms | - |
| Opening coil result 1 |  |  |  |  |  |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Pick-up time | 0 | 0 | 34.6 | ms | - |
| Ipmax | 0 | 0 | 1.25 | A | - |

| Opening coil result 1 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Designation | Min | Max | Value | Unit | Pass/Check |
| Aux | 0 | 0 | 48.95 | ms | - |
| De-energized coil | 0 | 0 | 49.9 | ms | - |
| Imax | 0 | 0 | 1.74 | A | - |